## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver4.0 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL | Select | Excess (+) | Less (-) | Excess (+) | Less (-)
Tender Inviting Authority: The Superintending Engineer, Institute Work Department, IIT(BHU), Varanasi
Name of Work:Electrical installations & SITC of DG Set Work in the. Nivedita , P.C Ray Hostel and New faculty apartment Block C&D IIT(BHU), Varanasi
Contract No: IIT(BHU)/IWD/ET-__/2025-26/____, Dated: ………………..
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P. |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P. | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT in Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | 1. Sub-head ‘A’ (Equipments) Providing, Installing, Testing and Commissioning of ‘Silent Type’ Diesel Generating set alongwith having Prime Power Rating of ——— KVA, 415 volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz, 3 phase system & for 0.85 Load Factor and consisting of the followings. a. Diesel Engine:Diesel engine 4 stroke water cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at 40 Degree C, 50% RH & at 1000 Meter MSL and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be fitted complete with all the required accessories. (b). Engine mounted Instrument Panel fitted with and having digital display for following: i. Start-stop switch with key ii. Water temperature indication. iii.Lubrication oil pressure indication. iv.Lubrication oil temperature indication. v.Battery charging indication. vi. RPM indication. vii. Over speed indication. viii Low lub. Oil trip indication ix. Engine Hours indication (c). Alternator :Synchronous alternator rated at ——— KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 40 Degree C, 50% RH & at 1000 Meter MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR conforming to IS: 4722/BS 2613 suitable for tropical conditions and with class- F/H insulation (d). Base Frame & Foundation: Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on suitable cement concrete foundation and vibration isolation arrangement as per recommendations of manufacturer. (e). Fuel Tank:Daily service fuel tank of —— liters capacity fabricated out of 3 mm thick M.S. sheet complete with all standard accessories and fuel piping between fuel tank and diesel engine with MS class ‘C’ pipes of suitable dia. Complete with valves, level indications & accessories as required as per specifications. (f). Exhaust System:Dry exhaust mainfold with hospital exhaust silencer and catalytic convertor. | [53 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | (g) Starting System12V/24V DC starting system comprising of starter motors: voltage regulator and arrangement for initial excitation complete with suitable nos. of batteries (25 plates, 180 Amp. Hour capacity lead acid type) as required as per specifications. (g)Accoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifications (h) Fabricating, Installing, Testing & Commissioning of automatic mains failure control including auto by-pass panel, suitable for ——— KVA silent type DG set complete with relays, timers, set of CTs for metering & protection and energy analyser to indicate currents, phase and line voltages, frequency, power factor, KWH, KVARH & provision for overload, short circuit, restricted earth fault, under frequency, control cabling from AMF panel to diesel engine and elsewhere if required, all complete and inter locking including the following: N Nos 200 Amps. 4 Pole ,MCCB ,25KA , 1 No. 200 Amps 4 pole onload changeover switch , power contactor- 200 amaps ,4 pole 415 volts 50 hz. with electrical interlock and realy 2 nos. Auto /Manual /Test (I) AMF Panel: Free standing floor mounted IP 42 automatic mains failure control panel including auto by-pass, suitable for KVA as below for silent type DG set complete with relays, timers, set of CTs for metering & protection and energy analyser to indicate currents, phase and line voltages, frequency, power factor, KWH, Kilo Volt Ampere Reative Hour (KVARH), KVA (Phase & Total), KW & provision for overload, short circuit, restricted earth fault, under frequency, power (aluminum) and control (copper ) cabling of suitable size upto 15 meter between AMF panel, LT Panel and DG Set including connection interconnection etc. as required, all complete and inter locking and communication/ Ethernet /RS485/SNMP port open protocol for BMS integration including suitable software, the panel shall be of DG Set OEM make etc. as per approved by Engineering in charge and including the following: 1. Suitable numbers and appropriate capacity 4 pole motorised electrically operated draw out with cradle type 3 position ACB/MCCB with electronic release for O/C & E/F and shunt trip. 2. Auto/Manual/Test/Off selector switch 3. Protection for under and over voltage phase reversal (2 nos Over voltage relay, 2 Nos. reverse power relay and 2 Nos. under voltage relay). 4. 3 Sets of current transformers 15 P 10 accuracy for protection and 15 VA class-I for metering 5. Energy analyser unit to indicate current, Voltage( L-N & L-L), kW, kVA (Phase & Total), Frequency, KWH, PF. | [53 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.02 | 6. LED Indicating lamps for load on mains and load on set. 7. Fuse/ MCB for instruments. 8. Battery charger, complete with transformer/ rectifier, D.C. voltmeter and ammeter, selector switch for trickle, off and boost and current adjustment. 9. Main supply failure monitor. 10. Supply failure timer. 11. Restoration timer 12. Control unit with three impulse automatic engine start/stop and failure to start lockout. 13. Impulse counter with locking and reset facility. 14. ON/OFF/Control circuit switch with indicator 15. Audio/Video annunciation for (i) High water temperature (ii) Low lubricating oil pressure (iii) Engine over speed (iv) Engine fails to start (v) Full load/maximum load warning 16. Protection for over/under Frequency, Loss of AC sensing, Over Current, Unbalancing load with suitable number of relays and accessories 17. Maintenance notification based on Engine Run Hour & due date. 18. Load Management through PLC to achieve auto opening and closing of incomer breakers, bus coupler switching of essential panel , interlocking providing signal to AMF Panel for load status and AMF shall give command to DG Set to auto start / auto stop depending upon load status and requirement etc. and necessary hardware and software required to perform the operation shall be provided by the contractor including all control wiring. Make-Cummins/Kirloskar/Greaves Cotton Ltd/Mahindra | [53 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.03 | SITC of 125KVA Silent DG Set Cofirming Latest standard BS 5514 ,ISO-3046 Alternator-IS-13364 (Part--ii),Genset-ISO 8528 with meeting CPCB -IV norms. |  | 1 | Nos. | 1445000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1445000 | 1445000 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.04 | SITC of 200 KVA Silent DG Set Cofirming Latest standard BS 5514 ,ISO-3046 Alternator-IS-13364 (Part--ii),Genset-ISO 8528 with meeting CPCB -IV norms. |  | 2 | Nos. | 2312000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4624000 | 4624000 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Supply and laying of Armoured Aluminium cable 650/1100V grade as per IS 7098(Part 1) 1988, PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of 1.1kV grade of following size in existing Trench/ RCC/ HUME / METAL pipe as required. MAKE-KEI/Gloster/Unversal/Polycab | [53 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.01 | 3.5C X 50 sq.mm |  | 80 | Mtrs | 826 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 66080 | 66080 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.02 | 3.5C X 95 sq.mm |  | 110 | Mtrs | 1241 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 136510 | 136510 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.03 | 3.5CX185 Sqmm |  | 180 | Mtr. | 1889 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 340020 | 340020 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | [53 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
3.01 | 150 mm width X 50 mm depth X 1.6 mm thickness Metre 531 |  | 80 | Meter | 625 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 50000 | 50000 | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
4 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | [53 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
4.01 | 3½ X 50 sq. mm (35mm) |  | 8 | Nos | 427 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3416 | 3416 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4.02 | 3½ X 95 sq. mm (45mm) |  | 4 | Nos | 608 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2432 | 2432 | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
5 | Supplying , installation testing and commissioning . TPN tap off box made of 1.6mm thick sheet steel encloser duly painted with powder coating on existing rising main complete wit TPN disconnector FSU and HRC fuse , connection , eartihing etc. as require | [53 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.01 | 100Amp Main Switch with HRC fuse Make-L&K/SEMINES/ ABB/Indoasean/C&S |  | 2 | Nos. | 14697 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 29394 | 29394 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
6 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. |  | 6 | Nos | 7092 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 42552 | 42552 | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
7 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. |  | 30 | Mtrs | 730 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 21900 | 21900 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Total in Figures | [51 empty] | 6761304 | 6761304 | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Note on K13: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K14: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K15: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K25: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K26: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K27: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K30: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information